Channel Access & Client Tools
Author:	Kenneth Evans, Jr., August 2004
Modified:	Kay Kasemir, October 2006
Andrew Johnson, January 2007 & 2011
Channel Access and Client Tools

---
EPICS Overview
EPICS Overview
MEDM
SDDS
BURT
Client
Probe
ALH
Channel Access
Server
IOC
IOC
IOC
Meter
Power Supply
Camera
Client Tools

---
Channel Access
Channel Access
- The EPICS “software bus”
- Used to read and write values to/from Process Variables
- To many people, Channel Access is EPICS
  - Especially those that have no IOC experience
  - “Integrate X into EPICS” often means “Be able to control X via CA”
- CA is not defined by a protocol specification
  - Jeff Hill (LANL) maintains the CA client and server libraries
  - A single expert maintainer for both ensures very robust control systems

---
What is a Process Variable (PV)
- “A named item of data, with associated optional attributes”
  - Data is an Integer, Floating point number, enumeration value or string, or an array of any of those types
  - Attributes include timestamp, alarm status/severity, precision, engineering units string, list of enumeration strings, operator/control/ alarm limits

---
Channel Access in One Slide
“connection request” or “search request”
“connection request” or “search request”
“get” or
“caGet”
“get” or
“caGet”
“put” or
“caPut”
“put” or
“caPut”
“set a monitor”
“set a monitor”
Who has a PV named “S1A:H1:CurrentAO”?
Who has a PV named “S1A:H1:CurrentAO”?
Change its value to 30.5
Change its value to 30.5
Notify me when the value changes
Notify me when the value changes
What is its value?
What is its value?
Channel Access Client
Channel Access Client
CA Client
CA Client
CA Server
CA Server
Channel Access Server
Channel Access Server
I do.
I do.
25.5 AMPS
25.5 AMPS
OK, it is now 30.5
OK, it is now 30.5
It is now 20.5 AMPS
It is now 20.5 AMPS
It is now 10.5 AMPS
It is now 10.5 AMPS
It is now -0.0023 AMPS
It is now -0.0023 AMPS
Process Variables:
Process Variables:
“put complete”
“put complete”
“post an event”
or
“post a monitor”
“post an event”
or
“post a monitor”
S1A:H1:CurrentAO
S1:P1:x
S1:P1:y
S1:G1:vacuum
S1A:H1:CurrentAO
S1:P1:x
S1:P1:y
S1:G1:vacuum
30.5 is too high. It is now set to the maximum value of 27.5.
30.5 is too high. It is now set to the maximum value of 27.5.
or
or
You are not authorized to change this value
You are not authorized to change this value
or
or

---
Tools Covered in This Presentation
Tools Described in This Presentation
- Base command-line tools
  - caget, caput, camonitor, cainfo
- Probe
- StripTool
- ALH
- MEDM

---
More Information
More Information
- There is a wealth of information in the EPICS web pages
  - http://www.aps.anl.gov/epics/index.php
- Each of the Extensions covered here has its own page there for
  - Documentation
  - Source code for the latest releases
- There are many other tools described there too
- Extensions executables are typically located at
  - …epics/extensions/bin/<platform>/<executable>
    - /usr/local/epics/extensions/bin/solaris-sparc/…
  - Platforms are solaris-sparc, linux-x86, linux-x86_64, win32-x86, etc.
- The Base command line tools are typically at
  - …epics/base/bin/<platform>/<executable>
    - /usr/local/iocapps/R3.14.11/base/3-14-11-asd1/bin/linux-x86_64/…

---
EPICS Extensions Web Page
EPICS Extensions Web Page

---
Command-Line Tools
Command-Line Tools
- There used to be several versions of these tools
- We will discuss the ones that now come with EPICS Base
- The tools we will cover are:
  - caget
    - Gets the value of one or more process variables
  - caput
    - Sets the value of one process variable
  - camonitor
    - Monitors the value changes of one or more process variables
  - cainfo
    - Gets information about one or more process variables
- All accept –h to display usage and options
NOTE: The programs with these names found in your default Unix search path are different (older).

---
Caget Example
Caget Example
Get the values of two process variables
caget S35DCCT:currentCC S:SRlifeTimeHrsCC
Returns
S35DCCT:currentCC 102.037
S:SRlifeTimeHrsCC 7.46514

---
Caput Example
Caput Example
Set the value of a process variable
caput Xorbit:S1A:H1:CurrentAO 1.2
Returns
Old : Xorbit:S1A:H1:CurrentAO 0
New : Xorbit:S1A:H1:CurrentAO 1.2

---
Camonitor Example
Camonitor Example
Monitor two process variables
camonitor evans:calc evans:bo01
Returns
evans:calc 2004-08-05 17:23:04.623245 1
evans:bo01 2004-08-05 17:23:04.623245 On
evans:calc 2004-08-05 17:23:05.123245 2
evans:bo01 2004-08-05 17:23:05.123245 Off
evans:calc 2004-08-05 17:23:05.623245 3
evans:calc 2004-08-05 17:23:06.123245 4
evans:calc 2004-08-05 17:23:06.623233 5
evans:calc 2004-08-05 17:23:07.123183 6
Use Ctrl-C to stop monitoring

---
Cainfo Example
Cainfo Example
Get information about a process variable
cainfo S35DCCT:currentCC
Returns
State: connected
Host: ctlapps4l188:5064
Access: read, no write
Data type: DBR_DOUBLE (native: DBF_DOUBLE)
Element count: 1
Some additional information can be found using Probe

---
Probe
Probe
- Simple way to get information about a single process variable
- Combines the features of caget, caput, camonitor, and cainfo in a graphical interface
- Very useful in diagnosing problems

---
Probe Demo
Probe Demo
Flash Demonstration of Probe

---
StripTool
- Plots process variables in real time on a strip chart
- Widely used

---
StripTool Demo
Flash Demonstration of StripTool

---
ALH
ALH
- Stands for Alarm Handler
- Important GUI application in the APS Control Room
- Brings alarms to the operators’ attention
  - It dings and flashes
- Can be configured to require the operator to acknowledge alarms
- Provides a hierarchical display
  - Allows managing alarms in overview or in detail
- Provides guidance for handling specific alarms
- Logs alarms and displays alarm history
The APS Operators configure the Alarm Handler

---
MEDM
MEDM
- Stands for Motif Editor and Display Manager
- The principal human interface to the APS control system
- Used worldwide at many facilities
- Creates and runs control screens
[Speaker Notes: 01/06/11]

---
MEDM Screens
MEDM Screens
And thousands of others

---
MEDM
- MEDM is very reliable at both design and run-time
- However it is very hard to extend
  - Uses the Motif X11 toolkit
  - Not written in Object-Oriented style
  - Ken Evans retired last year
- We will now only fix major bugs found in MEDM
  - Eventually it may prove impossible to build on new Linux versions
- Not a good choice for a new control system
  - There are several alternatives available
  - John Hammonds will talk about CSS and BOY on Thursday