## Slide 1: FRIB Controls Plan
Paul Chu FRIB Controls Group Leader (Acting)

## Slide 2: Outline
Overview
Global Timing System (GTS)
Machine Protection System (MPS)
Low-level controls
Global database and naming convention
User interface
High-level applications
Summary

## Slide 3: Overview
FRIB facts
  FRIB – Facility for Rare Isotope Beams
  Provide intense beams of rare isotopes to be used for cutting edge nuclear science research
  Total project cost of $614.5M fixed
  CW machine
  Superconducting cavities for acceleration, superconducting solenoids
  A Re-accelerator (ReA) to accelerate rare isotope beams produced by NSCL Coupled Cyclotron Facility
  EPICS based control systems
CD-4 milestone
  Accelerate multiple charge states of a heavy ion beam of 86Kr
  Measure FRIB driver linac beam with energy larger than 200 MeV/nucleon and beam current larger than 20 pA

## Slide 4: Project Status
Supported by U.S. Department of Energy and Michigan State University
CD-1 – Aug. 2010
CD-2 – Apr. 2012
CD-4
  Early finish date – end of FY2018
  Mid 2020
Currently under preliminary engineering design phase

## Slide 5: High Level Project Schedule
GOVERNMENT FISCAL YEAR
TPC covers schedule range
Arrows indicate targets for early construction with preliminary planning dates
CD-3a
8/1
2/3
2/3
2/28
10/02
10/29
Rev. 1/24/2011
Manage to early completion in 2018
FY
FY
FY
FY
FY
FY
FY
FY
FY
FY
FY
FY

## Slide 6: Facility Layout
uranium values given

## Slide 7: Driver Linac

## Slide 8: Controls Architecture
Device Controls (mag, RF, cryo…)
Global DB
Diagnostics
MPS and timing
Global Controls
UI
High-level apps
Alarm
Data Archive
E-log
Message logging
ESD
High-level control
Low-level control

## Slide 9: Top-level Requirements
Consistent look and feel among user interfaces
35 μs machine protection mitigation
Global timing system
Remote/manual control of devices/detectors
Model-based control
Integrated control room toolkit (e.g. snapshot/restore, alarm handler)
High availability as user facility
Notes: Must scale support 40k physical I/O connections and 300k process variables.
Fast BLM digitized at 100 kHz, i.e. up to 10 s of detecting time and 40 s of response time for MPS.
Diagnostics data taken at 10 Hz rate.

## Slide 10: Controls Highlights [1]
Global database
User interface
High-level applications
Central message logging
E-log
  IRMIS based e-log
Machine Protection System (MPS)
Global Timing System (GTS)
Low-level Control

## Slide 11: Controls Highlights [2]
Personal Protection System
Document traveler system
Software Configuration Management system
  Source repository
  Deployment system
  Bug report/track
Online document/help
Software development and test system

## Slide 12: Global Timing System
GTS status
  Internal review held on 4/6/2011
There will be one clock system (RF) and one timing system (triggers, real time data, and recovered clock when needed)
Timing requirement has to meet Diagnostics needs
Physics requirements defined

## Slide 13: Machine Protection System
MPS status
  Internal review held on 4/6/2011
  Physics requirements defined
MPS requirements
  Total MPS time budget = 35 s
    15 s for BLM detection and decision making
    10 s for MPS system reaction
    10 s for mitigation in place
  The interface between MPS and other subsystems is binary interface
  Diagnostics will generate binary OK/NOK signal with its internal knowledge
  MPS (Run Permit System and Fast Protection System) works closely with GTS to manage machine mode and beam mode

## Slide 14: Action Items from MPS Review
MPS and Timing detailed schedule including prototype (prior to procurement), field test etc. due by June review
Physics studies
  Fault study: If single cavity trips, what MPS reaction should be taken?
  Requirements from ESD (target) system for run permit system such as re-start scenarios
Timing system requirements – resolution and jitter
Physics requirements
  Surface damage calculation
  PRD due Apr. 30.
Inform other CAMs that BOEs must include MPS interface
Establish beam measurement requirements that define timing system needs; resolve multiple timing systems

## Slide 15: Low Level Controls Topology
Sensors
Instruments
Devices
PLC Controllers
EPICS
Soft IOC’s
Level 1 PV’s
Support Servers
Low Level Controls
~ 50K
Hierarchical PV’s
High Level Controls & Processes
> 200K
Machine Protection System Interlocks
Courtesy K. Davidson, J. Priller

## Slide 16: Network Topology
Outside World
FRIB Facility
High Level Controls
Low Level Controls
Devices
IOCs
PLCs
Control
PCs
Servers
Office
PCs
Servers
Firewall
Firewall
Firewall
Support
Servers
Maintenance PCs
Courtesy K. Davidson, J. Priller

## Slide 17: Global Database
SNS vs. IRMIS based approach
  In favor of IRMIS
    Up to date technology
    Better community support
    Fit our needs
IRMIS
  Device/Element tables modified from SNS schema
  API based access, no need direct SQL query
  Database access via service
  Collaborate with BNL
IRMIS 3 Schema

## Slide 18: Naming Convention
FRIB Naming Convention documented
FRIB and ReA should follow the naming rules
Signal name rules defined
Cable naming not defined yet
Naming will be enforced in DB

## Slide 19: Database Related Development
An IRMIS based e-log system prototyped
  Requirements collected
  E-log work planned
Electronic Document Traveler System
  Work flow control program
  SRF, Magnet and QA teams need this system
  Requirements collected
  Evaluating technologies and implement strategy

## Slide 20: User Interface
Eclipse base CSS is the choice for display manager
In-house expertise and full support from CSS colleagues around the world
CSS/BOY
CSS/Data Browser

## Slide 21: High-Level Applications (HLA)
Global and local coordinate systems for physics model
XAL based data structure
Data integration in DB
Online model support
  Better FRIB online model needed
  Work with Accelerator Physics for specs and detail plan
Software for commissioning and operation
Service-oriented architecture (SOA)
SOA example for HLA

## Slide 22: Summary
MPS and GTS PED in progress
Low-Level Control PED in progress
Database work started
  E-log prototyped
  E-traveler
High-level application and Online Model work planned