## Slide 1: EPICS @ DESY/ XFEL An Overview
EPICS Collaboration Meeting
San Francisco, October 5th, 2013
Matthias Clausen, DESY
Cryogenic Control Group

## Slide 2: Overview
Control Systems for the XFEL
News from Cryogenic Controls
CSS Developments
  Trent Plotter
  Synoptic Display Studio (SDS)
  CAJ – deadlocks
  DAL -> DAL-II
Alarm System
Archiver
IOC Redundancy

## Slide 3: XFEL: One Machine/ Three control systems
Schenefeld:
Science with X-ray flashes
DESY-Bahrenfeld:
Start of the3,4 km long XFEL
Osdorfer Born:
first split of the tunnel
Elektron-Accelerator
Creating X-ray Flashes

## Slide 4: The XFEL Tunnel

## Slide 5: The real XFEL Tunnel

## Slide 6: CSS Developments: Trend Plotter
Adding new features to Trend Plotter
Displaying archive deadband for each channel (Monitor Deadband for online/ live channel)
Interface to MySql Database

## Slide 7: CSS Developments: New SDS Widget: X/ Y Plot
Exyample of Cold Compressor Characteristic Diagramm

## Slide 8: CSS Developments: New SDS Widget: X/ Y Plot
Prototype of Cold Compressor Characteristic Diagramm

## Slide 9: CSS Lessions Learned: CAJ - deadlocks
CSS is running in the control room as primary operator interface
Over the last two years CAJ deadlocks were causing a lot of trouble
Communication with Matej improved:
  Prepared fixes make it into the code
  New bug fixes are distributed faster

## Slide 10: CSS Lessions Learned: DAL -> DAL-II
Lessions learned from DAL:
DAL is necessary to interface to several control system protocols
Support for metadata/ characteristics for several protocols requires a common interface
DAL-I was overloaded with too much functionality
Redefining requirements to the basic needs
A complete rewrite of the DAL layer is on the way

## Slide 11: Alarm System
Everything is a message
(alarm-; systemLog-; putLog-;snlLog;log4JLog…)
Messages are all transported as JMS messages
Messages can be displayed in tables (and trees)
Messages get written to Oracle (jms2Ora)
Messages become Alarms when processed in the Alarm Management System (AMS)

## Slide 12: Alarm System
Developments:
DAL2JMS – (now using DAL-II)
  Channel-Lists get monitored and written to JMS (as Message)
  Configuration similar to alh
Synchronized Alarm-Table/ Alarm-Tree
  Alarm Tree similar to alh Alarm Tree
AMS – Continuous improvement driven by control room
  Time based message filterns Generate alarm when state is active for more then ?seconds
  Attach alarm details to message and forward on different topic

## Slide 13: Archiver
Running in full production mode since March 2013
Basic requirements
Data retrieval for any interval takes no more than 3 sec
Display archive deadband for every channel
Implementation:
MySql Database on Sun Cluster
In addition to the ‚raw‘ data, we store mean values on a hourly and minute basis
Define ‚related‘ channels which archive the deadband of the main channel
Replace pvManager by DAL-II (1Q 2014)

## Slide 14: Redundancy
First mentioned during the EPICS Meeting at Argonne 2006:
2006 – Presentation:
From the preamble of the design specification:
… last and most importantly one major design goal must be matched:
Any redundant implementation must make the system more reliable than the non redundant one. Precaution must be taken especially for the detection of errors which shall initiate the failover. This operation should only be activated if there is no doubt that keeping the actual mastership will definitely cause more damage to the controlled system than an automatic failover.

## Slide 15: Redundancy: initial states
Ethernet
A
Ethernet
B
Ethernet
private link
Profibus - I
Profibus - II
IOC-A pref Master
C
P
U
Prof-I
Prof-II
IOC-B pref Slave
C
P
U
Prof-I
Prof-II
is:??
is:??
Ethernet
File Server

## Slide 16: Redundancy: Startup
Ethernet
A
Ethernet
B
Ethernet
private link
Profibus - I
Profibus - II
IOC-A pref Master
C
P
U
Prof-I
Prof-II
IOC-B pref Slave
C
P
U
Prof-I
Prof-II
is: booting
is: booting
Ethernet
File Server

## Slide 17: Redundancy: Running
Ethernet
A
Ethernet
B
Ethernet
private link
Profibus - I
Profibus - II
IOC-A pref Master
C
P
U
Prof-I
Prof-II
IOC-B pref Slave
C
P
U
Prof-I
Prof-II
is: Master
is: Slave
Ethernet
File Server

## Slide 18: Redundancy: Master CPU Failure
Ethernet
A
Ethernet
B
Ethernet
private link
Profibus - I
Profibus - II
IOC-A pref Master
C
P
U
Prof-I
Prof-II
IOC-B pref Slave
C
P
U
Prof-I
Prof-II
is: Master
is: Slave
Ethernet
File Server
Master CPU failure
Watchdog reset

## Slide 19: Redundancy: Master CPU Failure – Slave detects failure
Ethernet
A
Ethernet
B
Ethernet
private link
Profibus - I
Profibus - II
IOC-A pref Master
C
P
U
Prof-I
Prof-II
IOC-B pref Slave
C
P
U
Prof-I
Prof-II
is: Master
is: Slave
Ethernet
File Server
Master CPU failure
Watchdog reset
Reset Profi I + II
4. Slave detect master failure

## Slide 20: Redundancy: Master CPU Failure – Slave taking mastership
Ethernet
A
Ethernet
B
Ethernet
private link
Profibus - I
Profibus - II
IOC-A pref Master
C
P
U
Prof-I
Prof-II
IOC-B pref Slave
C
P
U
Prof-I
Prof-II
is: booting
is: Slave
Ethernet
File Server
7. Master CPU booting
Slave detect master failure
Start Master
Start Profibus I+II

## Slide 21: Redundancy: Master CPU Failure – Slave active/ pref master passive
Ethernet
A
Ethernet
B
Ethernet
private link
Profibus - I
Profibus - II
IOC-A pref Master
C
P
U
Prof-I
Prof-II
IOC-B pref Slave
C
P
U
Prof-I
Prof-II
is: booting
is: Slave
Ethernet
File Server
7. Pref Master CPU booting
8. Pref Master detect Master
9. Become Slave
Slave detect master failure
Start Master
Start Profibus I+II

## Slide 22: Redundancy: Master CPU Nettask Crash
Ethernet
A
Ethernet
B
Ethernet
private link
Profibus - I
Profibus - II
IOC-A pref Master
C
P
U
Prof-I
Prof-II
IOC-B pref Slave
C
P
U
Prof-I
Prof-II
is: Master
is: Slave
Ethernet
File Server
1. Nettask crash
Detect ‚special nettask case‘
Find existing Profi ‚stand by master‘
Stop Watchdog
Reset CPU and Profibus I+II
Detect Master is OFF
Profi Master still active
Cannot take over

## Slide 23: Redundancy: Master CPU Nettask Crash
Ethernet
A
Ethernet
B
Ethernet
private link
Profibus - I
Profibus - II
IOC-A pref Master
C
P
U
Prof-I
Prof-II
IOC-B pref Slave
C
P
U
Prof-I
Prof-II
is: booting
is: Slave
Ethernet
File Server
1. Nettask crash
Detect ‚special nettask case‘
Find existing Profi ‚stand by master‘
Stop Watchdog
Reset CPU and Profibus I+II
Detect Master is OFF
Profi Master still active
Cannot take over
9. Take over

## Slide 24: Redundancy
The current implementation is running since three years in three IOCs in production.
Production:
6kW@4K Helium plant
3MW primary compressor power
All (PID) control loops running in the IOC
SNL programs controlling sequences and supervisory control loops
PLCs only used for hardware interlock
helped us to survive 6 nettask crashes