## Slide 1: ITER AC/DC Converter Control System
2017. 5. 17
Rahk Sang Lee, Dawonsys
(ryanlee@dawonsys.com)
www.DAWONSYS.COM

## Slide 2: Contents
2. Control System for CCPS
1. Introduction
3. Control System for TFPS

## Slide 3: 1. Introduction
Location of Dawonsys

## Slide 4: 1. Introduction
The scope of this presentation is the I&C design and its implementation such as manufactured controllers, cubicles and verification scenarios for ITER AC/DC converter control system between Master Control System and Coil Power Supply and Distribution
Coil Power Supply and Distribution (CPSD) receives AC power from the GRID and supplies controlled DC power to the TF, PF, CS, CC & VS circuits. It shall also protect the coils by fast discharge of the stored energy in case of quench
Definition

## Slide 5: 1. Introduction
< ITER Coil Power Supply System Configuration >
ITER Power Supply System
TFPS
CCPS
PFCS
<Converter Specification>
CS = ±45 kA, ±1050V on-load
PF = ±55 kA, ±1050V on-load
VS = ±22.5 kA, ±1050V on-load
TF = 68 kA, ±650V/ ±160V on-load
CCU/L= ± 10 kA, ± 85V on-load
CCS= ± 10 kA, ± 300V on-load
<Load>
Dummy Load : 6.73mH/2.2 mΩ
TF : 17.7 H (Coil Inductance)
CS3U : 0.75929 H
CS2U : 0.75929 H
CS2L : 0.75929 H
CS3L : 0.75929 H
CS1 : 1.98136 H
PF1 : 0.70336 H
PF2 : 0.47477 H
PF3 : 1.8555 H
PF4 : 1.5607 H
PF5 : 1.5557 H
PF6 : 2.3901 H

## Slide 6: 1. Introduction
ITER I&C System
<Horizontal>
<Vertical>
ITER I&C Vertical System is composed with Central, Plant, Local Parts
ITER I&C Horizontal System is composed with conventional, Interlock, Safety Parts

## Slide 7: 1. Introduction
The CPSS MCS consists of Master Control (MRC), Circuit Control (CCR), Plant Interlock Control (PIC) and Plant Safety Control (PSC)
Master Control (MRC) is to interface with Plasma Control system and CCR through SDN and perform the function of coil power supply operation and integration
Circuit Control (CCR) is to supervise the LCCs for their operation states, monitoring data, etc. and distributes the voltage references from MRC to the corresponding LCCs
Plant Interlock Control is to take in charge of Central Interlock function and interface with Local Interlock Controllers
Plant Safety Control (PSC) is to take the responsibility of the occupational safety for the corresponding plant system and interface with Local Safety Controllers
Master Control System

## Slide 8: 1. Introduction
AC/DC Converters provide controlled DC current to the ITER magnet system and it is comprised of the line disconnector and earthing devices (AC and DC), converter transformer and phase controlled thyristor converter and sensors
The control system of AC/DC Converter consists of Sequential Controller (SEQC) or Interface Controller (INTFC), which communicates with CCR and plays a role of reference distribution and sequential control, and ALPHA Controller, which controls of thyristor converter, as for conventional control, and Local Interlock Controller (LIC) and Fast LIC (F-LIC) for local interlock control and Local Safety Controller (LSC)
Local Control System

## Slide 9: 1. Introduction
Master Control System I&C has functional interface with AC/DC Converters for monitoring, control and protection of Coil Power Supply System
Functional interfaces:
  Monitoring and control data
  Dispatching voltage reference
  Converter status information forward
  Coordination of CVOS
  TF converter operation (only for TFPS MCS)
  To connect to other plant systems for monitoring and control
  Perform fast discharge interlock function
  Perform bypass loop interlock function
  Integrated interlock function of Coil Power Supply System
  Investment protection for the AC/DC Converter
  Perform central occupational safety function
  Occupational safety protection of the AC/DC Converter
Control Functions

## Slide 10: 2. Control System for CCPS
< Configuration of CCPS FAT >
FAT Configuration
※ FAT : Factory Acceptance Test

## Slide 11: 2. Control System for CCPS
< Configuration of CCPS FAT in Local Side>
Layout of CCU/L Converter
Control
Cubicle
Converter
Bridge
AC busbar
CCWS
Manifold
DC Inductor
Bypass
Switch
DCDS
DC Interconnecting
Busbar
DCES
Fire wall

## Slide 12: 2. Control System for CCPS
Manufactured System
mini-CIS
Interlock Cubicle
(41MC00-CU-2003)
Conventional Cubicle
(41MC00-CU-1003)
Test Terminal
(mini-CODAC)
LCC Simulator
Industrial PC x 1
S7-400 PLC x 2
ET-200M Remote IO x 2
DLIB x 3
<Front & Rear View of Conventional Cubicle>
<Front & Rear View of Interlock Cubicle>
Manufactured Master Control System for FAT

## Slide 13: 2. Control System for CCPS
Type Test Procedure
  To verify the hardware and mechanical parts of MCS cubicle are well assembled and operate properly and functions of each components are well implemented according to their requirements
  Cubicle Unit Test
    The appearances with no damage and the wiring
    Wires are well-connected with each other and well opened with neighbor wires and earth
    Normal condition after initialization and ready for operation
    Digital in/output signal could be read/set properly
  Configuration Test
    To verify that the installed firmware/software package and configuration parameters are valid
  Component Test
    PSH functions: plant system PVs, SYSMON PVs, HMU PVs
    MRC functions: MRC PVs, voltage control, current control with no coupling, real-time transmission, transmission of converter status information, co-ordination of current return to zero, data archiving
    CCR functions: CCR PVs, monitoring and control data, dispatching voltage reference, converter status information forward, transient recorder management, co-ordination of converter operational states
    PIC functions: PIC PVs, F-PIC PVs, hardwired signals, network redundancy

## Slide 14: 2. Control System for CCPS
Performance Test Procedure
  Conceivable test cases in the environment of all the relevant components installed and running without a problem
  Plant System Test
    Conventional : State machine, voltage control, current loop control with no coupling, coordination of current return to Zero,
    Interlock: : Power permit, Converter Fault, Fast discharge, Usage for CPU and Memory , Alarm Test, Archive Test, Log Test.
  Network Performance Test
    The transmission delay within the MCS system and/or caused by the converters and its local controllers.
  Endurance Test
    To check that the MCS operates properly over a long period of time.
    The full plasma operation scenario is performed repeatedly. If some errors occurred, then the operation scenario will be stopped immediately and reported error cause.
  Stress Test
    To check interlock actions is occurred, one of PIN/CIN network is disconnected.

## Slide 15: 2. Control System for CCPS
HMI – Data Browser
  Any PV registered with archiving property can be investigated using the data browser.
  This screen shows the archived values for PSOS OPREQ and PSOS OPSTATE.
  The figure on the right shows the magnified view for one cycle.
< Cycle of the operation Scenario >

## Slide 16: 2. Control System for CCPS
Voltage Control
< Voltage reference from PCS simulator >
< Voltage/current value from converter >
  The voltage reference is sent from PCS over SDN, and retrieved by MRC and then sent to subordinate CCR over SDN, The CCRs send this value to subordinate LCC over local Ethernet interface (1KHz)
  Voltage reference from the PCS simulator together with the converted reference by MRC
  Coil Voltage and coil current which are read from the converter.
    The coil current follows the shape of the voltage reference from the PCS simulator, between -10kA and 10kA.
  - PCS Reference : Voltage reference received from the PCS
  - CVT Reference : Voltage reference transmitted to the converter
  - V Coil : Coil voltage value read from the converter
  - I Coil : Coil current value read from the converter

## Slide 17: 2. Control System for CCPS
Current Loop Control
< Data browser screen of the archived data >
< oscilloscope image captured at the converter side >
  This test verifies composite functions by checking PVs for voltage reference and current values at the LCC (1KHz)
  The current reference from the PCS simulator, converted voltage reference from MRC, coil current value from the converter
  The magnified view at the converter side captured using an oscilloscope

## Slide 18: 2. Control System for CCPS
FAT Sketch
Duration: 9th ~ 11th Dec. 2015
Location: Dawonsys factory (Ansan)

## Slide 19: 2. Control System for CCPS
HMI – Converter Operation
Duration: 9th ~ 11th Dec. 2015
Location: Dawonsys factory (Ansan)
COS/PSOS State
Converter Status
Critical Interlock Status
Alarm Status
Additional Status
Navigation Bar
Non-critical Interlock Status
Operation Commands

## Slide 20: 3. Control System for TFPS
FAT Configuration
< Configuration of TFPS FAT >

## Slide 21: 3. Control System for TFPS
Manufactured System
Manufactured Master Control System for FAT

## Slide 22: 3. Control System for TFPS
제어기 기술 확립
Analog to Digital Converting Controller
- 18 bit ADC
- 18 Channel
Alpha Controller
Xilinx ZYNQ (7045)
RTOS
Relay IN : 27 ch
Relay OUT : 14 ch
Fiber IN : 44 ch
Fiber OUT : 52 ch
Sequential Controller
Xilinx ZYNQ (7045)
Linux
<Conventional Cubicle>
Manufactured Local Control System and RTDS
Manufactured System
<LCC Simulator>
<RTDS System>
※ RTDS : real time power system simulator

## Slide 23: 3. Control System for TFPS
제어기 기술 확립
Test Scenario
Charge
mode
Sustain
mode
Discharge
mode
Accelerated discharge
0.5hour
Icoil
68 kA
4hour
Tap change
(650V tap)
Zero
current
15s
0.5hour
55 kA
35 kA
15 kA
0.45h
0.35h
1.2h
0.2h
0.6h
0.2h
1h
T1
T2
T3
T4
TF coil current (commend)
Bypass switch current
Accelerated discharge command (MCS → LCC)
TFPS Test Scenario for Integrated Test (MCS, LCC and RTDS)
  Execute the sustain mode during charge mode
  Execute the accelerated discharge during normal operation
※ RTDS : real time power system simulator

## Slide 24: 3. Control System for TFPS
제어기 기술 확립
Integrated Test
Duration: 25th ~ 28th Apr. 2017
Location: National Fusion Research Institute (NFRI) (Daejeon)
1 KHz Operation
< Master Control System HMI >
< Raw Data from Converter captured by Oscilloscope >
Coil Current
Reference from Upper System
Coil Current
Bridge Current
Bypass Current
Accelerated Discharge
Accelerated Discharge

## Slide 25: Appendix
Manufactured VS1-1 Converter in Dawonsys Factory
Manufactured VS-1 Converter
<VS1 Converter in Factory>