## Slide 1: New controller F3RP71 for EPICS IOC
Product Update
Yutaka Kubota
Edge Controller Section, International Sales Dep.,
Control Instruments Sales Division, Product Sales Center, IAPS BHQ
YOKOGAWA ELECTRIC CORPORATION
18 May. 2017

## Slide 2: Two types of Controller
Sequence CPU
  Cyclic execution Engine
    VITESSE Engine
  Unique Ladder
    Object Ladder
    Macro Block
    Script Coding
  Sensor control block
  Unique environment
Real-time OS CPU
  RTOS (Real time Linux)
  C/C++ Language
  Easy to reuse Program
    Library, Middleware
  Multi task function
  Standard interface

## Slide 3: Product Roadmap
1995
2010
2005
2000
2020
SP20/30/21/25/35 / Original ASIC
( SPU )
F3RP4 Series / General-Purpose Processor
( SH4 : 200MHz )
F3SP6x Series / Original ASIC
( SPU2 )
SP28/38/5x / Original ASIC
( SPU2 )
F3RP6 Series / General-Purpose Processor
( PowerPC : 533MHz )
F3SP7 Series / Original ASIC
( SPU3 Vitesse Engine )
F3RP5 Series / General-Purpose Processor
( SH4 : 240MHz )
2015
S/W Logic
H/W Logic
C Language Controller
Sequence Controller
Utility
Module
F3RP7 Series / General-Purpose Processor
( ARM A9: 866MHz x2 )
2001~
2004~
2007~
2015~
LD
F3RP9 Series / General-Purpose Processor
( ARM A53: 1.3GHz x2 + R5 533MHz x2 )
Utility
Module

## Slide 4: EPICS on e-RT3 2.0
EPICS built in F3RP61-2L gives us many benefit
・Save engineering cost and time ・Save production cost
・Save TCO ・Improve reliability of system
・Stable delivery of products
OPI
IOC
Network-Based Controller
Proprietary Protocol
Channel Access
VME or PC
OPI
Network-Based Controller(IOC)
Channel Access
EPICS
EPICS
EPICS & Data handler
F3RP61-2L
Hardware
Linux & Driver
EPICS (IOC)
EPICS built in
It is the result of good collaboration with KEK and Yokogawa.

## Slide 5: Simple usage under EPICS
Conventional PLC usage with asynchronous access
FAM3 PLC
I/O Modules
F3RP61
IOC
FAM3 PLC
I/O Modules
Ladder CPU
(Logics)
OPI
CA Clients
IOC
(Logics)
PLC usage with F3RP61 with only synchronous access and maybe with sequencer
OPI
CA Clients
FAM3 PLC
I/O Modules
F3RP61
IOC
If necessary, we can combine
OPI
CA Clients
Ladder CPU

## Slide 6: Installation in Accelerator system

## Slide 7: F3RP7X Series

## Slide 8: Differences from existing products
4/5 Series
6 Series
7 Series
Usability/Flexibility
Expandability
Storage
Network
Processor
Supported OS
VxWorks / NORTi / WinCE (RP4□)
VxWorks / NORTi / OS-9 (RP5□)
SH4 7750S 200MHz (RP4□)
SH4 7750R 240MHz (RP5□)
10BASE-T/100BASE-TX
1 Port
Linux / VxWorks
PPC MPC8347E 533MHz
10BASE-T/100BASE-TX
2 Port
CF Card
1 Slot
PCI Bus (32 bit)
Linux / VxWorks
ARM Coretex-A9 866MHz Dual
10BASE-T/100BASE-TX/1000BASE-T
2 Port
SD Card (SDHC)
2 Slot
PCI Bus (32 bit)
FPGA installed
CPU Setting Tool / Device Monitoring Tool
Smart Access / Preinstalled OS/OSS
PC Card
1 Slot
New

## Slide 9: Specification
 |  | F3RP71-2L |  | F3RP71-1R | F3RP61-2L | F3RP61-2R
CPU | Core | ARM Cortex-A9 MPCore（Dual Core） |  |  | MPC8347E | 
 | 動作周波数 | 866MHz |  |  | 533MHz | 
 | Cache | L1：32KB I/D L2：512KB |  |  | L1：32KB I/D | 
 | 拡張 | NEON™および単精度／倍精度の不動小数点 |  |  | 単精度／倍精度の不動小数点 | 
Endian |  | Little endian |  |  | Big endian | 
OS |  | Linux3.18.16 + pach-3.18.16-rt13 |  |  | Linux2.6.26.8 + pach-2.6.26.8-rt1 | 
Memory | NOR FLASH | 256MB | 128MB |  | 64MB | 64MB
 | DDR3 SDRAM | 1GB | 256MB |  | 128MB | 128MB
 | SRAM | 8MB | なし |  | 4MB | なし
I/F | Ethernet | 1000BASE-T／100BASE-TX／10BASE-T 2 port |  |  | 100BASE-TX／10BASE-T 2 port | 
 | RS-232C | 9.6kbps～115.2kbps 1 port |  |  |  | 
 | Strage | SDHC（最大32GB） 2 slot |  |  | CF 1 slot | 
 | PCI | Utility module用（32bit） |  |  |  | 
 | その他 | JTAG（専用10pin connector） |  |  | JTAG（専用10pin connector）、IEEE1394 | 
RAS機能 | 電源断検出 | 入力電源断を検出、Applicationへ通知 |  |  |  | 
 | Watch dog timer | Application software動作状態のmonitor |  |  |  | 
 | SD card異常検出 | 過電流保護回路搭載 |  |  |  | 
 | FAIL信号出力 | あり |  |  |  | 
RTC |  | 年、月、日、時、分、秒、曜日（Battery backup） |  |  |  | 
Status LED |  | RDY,RUN,ALM,ERR,COM,SD1,SD2,BAT,U1,U2,U3,OS,1,2,4,8 |  |  | RDY,RUN,ALM,ERR,COM,CF,LNK1,LNK2,100,BAT | 
Switch |  | MODE switch／SET switch |  |  |  | 
最大実装Module数 |  | 4 module／1 unit |  |  |  | 
消費電流 |  | 1200mA |  |  |  | 
外形寸法 |  | 28.9(W)×100(H)×83.2(D)mm |  |  |  | 
質量 |  | 220g |  |  | 200g | 
New
New

## Slide 10: CPU Block Diagram

## Slide 11: e-RT3 Plus “Basic Performance”
Dual Core Processor
  Throughput speed 4.3x
Real-time performance
  Latency（Up to 105x）
  Jitter（≦ x1/2 ）
Memory capacity
  Flash ROM（max 4x）
  SDRAM（max 8x）
  SRAM（max 2x）
Gigabit Ethernet [2 port]
SD Card [2 slot]
I/O access speed up
※Flash ROM
data使用用途
※Linux性能
比較demo
※processor処理
性能比較（実測値）
Performance Test
MODE S/W
10BASE-T/
100BASE-TX/
1000BASE-T
PCI Bus
SDHC
SDHC
RS-232C
Set S/W
Maintenance
LED
New

## Slide 12: e-RT3 Plus “Accessible / Visible”
Preinstall Linux system（Kernel, Device, OSS etc.）
Application development on Windows
Install time
（Linux system）
F3RP61
Install time（OSS）
Application Development
F3RP71
New
Application Development
START
START
GOAL
F3RP61
F3RP71
New
Web maintenance tool
host machine
Linux OS
Windows OS
Linux OS
host machine

## Slide 13: e-RT3 Plus “Applicable”
Applicable controller by OSS
  APACHE（HTTP Server ）
  PHP（script language）
  TCPDF（Reporting）
  CUPS（printer server）
  PostgreSQL, SQLite3（Database）
…
Logger
Monitoring
Process Control
Inline Instrumental
Intelligent gateway
Machine control
Over 90 kinds of OSS
※Open Source Software

## Slide 14
Thank you for your attention.

## Slide 15: Appendix

## Slide 16: Processor performance test
533MHz Single
866MHz Dual
Chart: [sec]
| F3RP71 SMPあり | F3RP71 SMPなし | F3RP61
系列 1 | 13.206 | 26.433 | 41.301
Executing Time of
10 Subtraction Processes（0xFFFFFFF times）
x３.13
1000 Mips
4330 Mips
F3RP61
F3RP71
4.3x speed
New

## Slide 17: Latency

## Slide 18: Performance
Drawing speed competition
  Plot points
    1266
  Load Application
    Subtractionprocess x 10
  Processing time
    1min
挑戦者
2007 ~
New
2016 ~
VS
ペン
?
XY Stage
Pencil

## Slide 19: Performance
2007 ~
VS
WIN
New
2016 ~

## Slide 20: Jitter
VxWorks
Linux
RP7 Series
RP6 Series
140[us]
60[us]
60[us]
90[us]
Reference data

## Slide 21: I/O access time
Relay access time
Register access time
I/O interrupt response time
 | Input |  | Output |  |  | 
 | Read |  | Read |  | Write | 
 | 1 word | 2 word | 1 word | 2 word | 1 word | 2 word
F3RP71 | 8.602 | 8.632 | - | - | 13.781 | 24.471
F3RP61 | 12.712 | 12.722 | 12.681 | 19.977 | 19.175 | 33.095
 | Read |  |  |  | 
 | 1 word | 8 word | 10 word | 64 word | 100 word
F3RP71 | 8.296 | - | 50.491 | - | 472.436
F3RP61 | 11.119 | 51.701 | - | 376.048 | -
 | Linux |  | VxWorks | NORTi
 | F3RP71 | F3RP61 | F3RP62 | F3RP5x-3P
Response time（Min） | 94 | 110 | 95 | 60
Response time（Max） | 136 | 195 | 115 | 70
Average | 107 | - | - | -
 | Write |  |  |  | 
 | 1 word | 8 word | 10 word | 64 word | 100 word
F3RP71 | 8.479 | - | 51.164 | - | 477.343
F3RP61 | 10.903 | 50.008 | - | 363.036 | -
[us]
[us]
[us]
[us]
Read x1.5
Write x1.4
Read ≒ x1.3
Write ≒ x1.2
Respond as fast as
RP62（VxWorks）

## Slide 22: Development host machine Environment
Xilinx SDK（Windows／Linux）
  Application Development
  Execution／Debug（Remote）
  File transfer etc.
eclipse
Xilinx SDK
User can download the install file,7 Xilinx SDK ‘ from below URL http://www.xilinx.com/support/download/index.htm
Software Development Kit（Vivado 2013.4: Stand alone SDK single package）
Install file size ： ≒2GB
Download
From
Yokogawa or Xilinx Web site
Windows OS
（Windows 7 32bit/64bit）
Linux OS
（CentOS 6.7 32bit）

## Slide 23: Web maintenance tool
Device monitor
  CPU module monitor
  I/O device monitor
  Comment file
CPU config.
  Top／Login
  Service
  User setting
  IP address setting
  Calendar／Time setting
  Start script
  Memory・Log
  Device setting
Display Instruction Manual
Web browser
Web server mounted
LAN cable

## Slide 24: Open Source Software list（90種類）
No. | Package name | Version | License | No. | Package name | Version | License | No. | Package name | Version | License
1 | apache2 | 2.4.10 | Apache License v2.0 | 31 | libiconv | 1.11.1 | LGPLv2 | 61 | php-fpm | 5.6.4 | PHP-3.01
2 | bash | 4.3.30 | GPLv3 | 32 | eglibc-gconv | 2.19 | GPLv2, LGPLv2.1 | 62 | php-fpm-apache2 | 5.6.4 | PHP-3.01
3 | bison | 3.0.4 | GPLv3 | 33 | libiodbc | 3.52.10 | BSD, LGPLv2.1 | 63 | poppler | 0.35.0 | GPLv2
4 | chkconfig | 1.3.63 | GPLv2 | 34 | libsysfs (sysfsutils) | 2.1.0 | GPLv2, LGPLv2.1 | 64 | popt | 1.16 | MIT
5 | coreutils | 8.23 | GPLv3 | 35 | termcap | 2.0.8 | GPLv2 | 65 | postgresql | 9.4.0 | PostgreSQL
6 | cracklib | 2.9.2 | LGPLv2.1 | 36 | libuser | 0.60 | LGPLv2 | 66 | postgresql-client | 9.4.0 | PostgreSQL
7 | cups | 2.0.2 | GPLv2, LGPLv2 | 37 | logrotate | 3.8.8 | GPLv2 | 67 | procps | 3.2.8 | GPLv2, LGPLv2
8 | dhclient | 4.3.1 | ISC | 38 | mktemp | 1.7 | ISC | 68 | psmisc | 22.21 | GPLv2
9 | diffutils | 3.3 | GPLv3 | 39 | module-init-tools | 3.15 | GPLv2 | 69 | pure-ftpd | 1.0.36 | BSD
10 | dosfstools | 3.0.26 | GPLv3 | 40 | mtd-utils | 1.5.1 | GPLv2 | 70 | python | 2.7.3 | PSFv2
11 | e2fsprogs | 1.42.12 | GPLv2, LGPLv2, BSD, MIT | 41 | mtd-utils-jffs2 | 1.5.1 | GPLv2 | 71 | readline | 6.3 | GPLv3
12 | e2fsprogs-libs | 1.42.12 | GPLv2 | 42 | ncurses | 5.9 | MIT | 72 | rpcbind | 0.2.2 | BSD
13 | ethtool | 3.18 | GPLv2 | 43 | net-tools | 1.60+26 | GPLv2 | 73 | rpm*1 | 5.4.14 | LGPLv2.1
14 | findutils | 4.4.2 | GPLv3 | 44 | nfs-utils-client | 1.3.1 | GPLv2 | 74 | sed | 4.2.2 | GPLv3
15 | flex | 2.5.39 | BSD | 45 | ntp | 4.2.8 | NTP | 75 | shadow | 4.2.1 | BSD, Artistic-1.0
16 | foomatic-filters | 4.0.17 | GPLv2 | 46 | ntp-utils | 4.2.8 | NTP | 76 | sqlite3 | 3.8.8.3 | PD
17 | freetds | 0.92.79 | GPLv2 | 47 | ntpdate | 4.2.8 | NTP | 77 | sudo | 1.8.9p5 | ISC, BSD, Zlib
18 | inetutils-ftp | 1.9.2 | GPLv3 | 48 | ntpd | 4.2.8 | NTP | 78 | sysklogd | 1.5 | GPLv2, BSD
19 | gawk | 4.1.1 | GPLv3 | 49 | openssh | 6.7p1 | BSD | 79 | sysvinit | 2.88dsf | GPLv2
20 | gdbserver (gdb) | 7.8.1 | GPLv3 | 50 | openssh-misc | 6.7p1 | BSD | 80 | tar | 1.28 | GPLv3
21 | glib-2.0 | 2.43.2 | GPLv2, LGPLv2 | 51 | openssh-sftp | 6.7p1 | BSD | 81 | tcpdf | 6.2.6 | GPLv3
22 | grep | 2.21 | GPLv3 | 52 | openssh-sftp-server | 6.7p1 | BSD | 82 | inetutils-telnet | 1.9.2 | GPLv3
23 | gzip | 1.6 | GPLv3 | 53 | openssl | 1.0.1j | OpenSSL | 83 | inetutils-telnetd | 1.9.2 | GPLv3
24 | initscripts | 1.0.0 | GPLv2 | 54 | libpam | 1.1.8 | BSD, GPLv2 | 84 | unixodbc | 2.3.2 | GPLv2, LGPLv2.1
25 | iproute2 | 3.18.0 | GPLv2 | 55 | pam-plugin-cracklib | 1.1.8 | BSD, GPLv2 | 85 | util-linux | 2.25.2 | GPLv2, LGPLv2.1, BD
26 | iptables | 1.4.21 | GPLv2 | 56 | passwd | 0.79 | BSD, GPLv2 | 86 | vim-tiny | 7.4 | Vim
27 | iputils | s20121221 | BSD, GPLv2 | 57 | pciutils | 3.3.0 | GPLv2 | 87 | cronie | 1.4.12 | ISC, BSD, GPLv2
28 | less | 458 | GPLv3, BSD | 58 | perl | 5.14.3 | Artistic-1.0, GPLv1 | 88 | xinetd | 2.3.15 | BSD
29 | libcap | 2.24 | BSD, GPLv2 | 59 | php | 5.6.4 | PHP-3.01 | 89 | zile | 2.4.11 | GPLv3
30 | libgcc | 4.7.3 | GCC RLE v3.1, GPLv3 | 60 | php-cli | 5.6.4 | PHP-3.01 | 90 | zlib | 1.2.8 | Zlib