## Slide 1: ITER & CODAC Core System Status Update
Ralph Lange Control System Division ITER Organization
Disclaimer: The views and opinions expressed herein do not necessarily reflect those of the ITER Organization.
Disclaimer: The views and opinions expressed herein do not necessarily reflect those of the ITER Organization.

## Slide 2: Outline
Overview and Status
  Architecture, Networks, Infrastructure
  Standardization: Specification, Hardware, Software, Support
  Central Systems and Applications
Challenge 1: Control with no Building
  Integration Schedule
  Mitigation of Controls Building Delay
Challenge 2: Scale
  Example: Nuclear Safety
  Example: Cubicles (19” racks) and Buildings

## Slide 3: Overview and Status
Update

## Slide 4: High Level Requirements
The ITER control system
performs the
functional integration of the ITER plant
and
enables integrated and automated operation

## Slide 5: Architecture

## Slide 6: Architecture
Breakdown in 18 ITER control groups (CBS level 1) covering 28 PBS
An ITER control group contains many Plant System I&C, total no. 171 (CBS level 2)
A Plant System I&C is a deliverable from a procurement arrangement (IN-KIND)
A procurement arrangement delivers a part, one or many Plant System I&C
CBS 1
CBS = Control Breakdown Structure
CBS 2

## Slide 7: Interfaces
171 local Control Systems (so-called Plant Systems I&C) scattered and supplied by 101 Procurement Arrangements covering 28 PBS
Challenge:
Integration

## Slide 8: Standardization
Documentation – Plant Control Design Handbook (PCDH)
  Specifications, guidelines, catalogues
Hardware
  cubicles, controllers, input/output, network interfaces
Software (common open source framework)
  CODAC Core System
Instrumentation & Control Integration Kit
  Distributed for free to all plant system I&C

## Slide 9
The base software for ITER Control System released once or twice per year and providing common services like:
Communication
Configuration
Human Machine Interface
Archiving
Alarming
Input/output device drivers
….
CODAC Core System

## Slide 10
Distributed to all plant system suppliers
154 instances at 63 organizations
Maintained and upgraded throughout ITER lifetime
Supported by
CCS Hands-On workshop at IO and DA premises
CCS Training in IO On-Line Learning Center
Help-desk : codac-support@iter.org
IO’s RedHat Network Satellite
Server
Development & Tests
Published
Versions
Internet
CODAC Core System

## Slide 11: Human Machine Interface Standardization
Plant System operator workstation: 3 screens, 1 keyboard/mouse
  Ultra high definition resolution 3840 x 2160 (4K) at 60Hz
  24 inches
  Aspect ratio of 16:9

## Slide 12: CODAC Operation Applications
CODAC Operation Applications are ITER dedicated software packages deployed on dedicated central servers
Execution
Control (PCS) Supervision (SUP)
Preparation
Scheduling (PSPS) Gateway (ORG)
Analysis
Data handling Data access
eXternal to POZ

## Slide 13: Infrastructure
ICH/
ECH
Cooling water
Control building
Backup control building
Electrical
Coil power supplies
Tokamak complex
Cryoplant
Neutral beam
Hot cell

## Slide 14: Infrastructure
Redundant dual star configuration
All cables end up in B71 and B24
Bill of Material
173 cubicles
175 passive network panels
300 km multi-core single mode
170 km multi-pair copper cables
Connecting thousands of plant system I&C client cubicles via network panels located in 28 buildings

## Slide 15: Schedule
ITER 2016 baseline approved by ITER Council in November 2016
Underpinned with detailed resource loading
Staged approach
First Plasma (FP)
Dec. 2025
FP Finished and Start of Assembly II
Jun. 2026
End of Assembly II
Jun. 2028
Start of Pre-Fusion Power Operation-I (SP)
Dec. 2028
End of Pre-Fusion Power Operation-I and Start of Assembly III
Jun. 2030
End of Assembly III
Sep. 2031
Pre-Fusion Power Operation-II (TP)
Jun. 2032
End of Pre-Fusion Power Operation-II and Start of Pre- Nuclear Shutdown for Assembly IV
Mar. 2034
End of Pre-Nuclear Shutdown for Assembly IV
Mar. 2035
Fusion Power Operation
(DT)
Dec. 2035
Engineering Operation (SC Magnets)
(6 Months)
Assembly II
(24 Months)
Integrated Comm. II (6 Months)
Pre-Fusion Power Operation-I (18 Months)
Pre-Fusion Power Operation-II (21 Months)
Assembly IV (12 Months)
Integrated Comm. IV (9 Months)
Integrated Comm. III (9 Months)
Assembly III (15 Months)
add 46 add 29 add 18
plant system I&C plant system I&C plant system I&C

## Slide 16: Control with no building
Challenge 1

## Slide 17
Dependency on plant system I&C installation and site acceptance test
Dependency on buildings availability
Deliveries to project (plant system I&C and site)
Design of central control systems almost complete
Schedule

## Slide 18
Control building (B71)
Schedule

## Slide 19
Requirements
The central infrastructure and services must be available soon
Human Machine Interfaces must be provided for plant system I&C integration
Migration of all plant systems I&C control to B71 must be achieved within 18 months
Implementation
Create temporary local autonomous “islands” in strategic buildings, providing central services and Human Machine Interfaces
Connect islands with temporary cables to provide inter building connectivity
Maximize emulation of final system to simplify migration to B71
Mitigation – Temporary Control Rooms

## Slide 20
The following functions are provided as services to the plant systems:
Human Machine Interface
Data handling including archiving, storage and access
Inter plant communication
Role based access control
Alarm handling
Time synchronization
Electronic logbook
Access to central software repository and issue tracking (configuration control)
Development stations for software updates (fast turn-around)
Central supervision and monitoring
Access to archived data from office
Temporary Control Rooms – Functions

## Slide 21
Install central servers in existing CODAC network cubicles
Standard HMI stations in suitable room
Add Interlock and Safety when applicable (local test tools)
Cover all Plant Systems for First Plasma (before Control Building availability) by eleven Temporary Control Rooms
Temporary Control Rooms – Implementation

## Slide 22
Temporary Control Rooms – Schedule

## Slide 23
First Temporary Control Room in Building 36 (electrical) powered up
I&C Integration and Commissioning starts NOW
Temporary Control Rooms – Status

## Slide 24: Scale
Challenge 2

## Slide 25: Example: Nuclear Safety
24.1 m/s2 at the shaking table
101 m/s2 in heaviest sampler
Confinement of radioactive material
Protection from exposure to ionizing radiation
Two separate signal chains
Extensive qualification of components
Cost per signal:
Fission reactor: ~3,000 € (proprietary hw)
ITER: ~1,500 € (commercial hw)
Number of signals:
Fission reactor: 200-400
ITER: 40,000

## Slide 26: Example: Cubicles and Buildings
How many 19” racks do you have in your facility?
ITER will have about 3,500 cubicles, each equipped with a PLC that is monitoring the cubicle status
With an EPICS database of 20 records per cubicle, that’s 70,000 records just for cubicle monitoring
The building integrator plans to install pretty large PLCs (S7 1518) with up to > 50,000 signals per PLC

## Slide 27: Thank you ps. Check out the drone flight videos!